| Customer | : ................................................................................... |  |
| --- | --- | --- |
| Software | : ICDAS 2.1 |  |
| Base Version No. | : 2.1 |  |
| Released Version No. | : 2.1.1 |  |
| System Location | : .................................................................................. |  |
| Protocol Pre Approval |  |  |
| Prepared By: | Name : ..................................................... Sign : ..................................................... Date : ..................................................... | Company ...................................................................... |
| Reviewed By: | Name : ..................................................... Sign : ..................................................... Date : ..................................................... | Company ...................................................................... |
| Approved By: | Name : ..................................................... Sign : ..................................................... Date : ..................................................... | Company ...................................................................... |
| Test Execution Details |  |  |
| Test Executed By: | Name : ..................................................... Sign : ..................................................... | Company ...................................................................... |
| Test Verified By: | Name : ..................................................... Sign : ..................................................... | Company ....................................................... |
| Test Date | Start of Test ................/...................../................... (dd/mmm/yyyy) | End of Test ................/...................../................ (dd/mmm/yyyy) |

Contents:

1	Introduction	4

2	Protocol Pre approval	4

3	Brief Description	4

4	Purpose	4

5	Test procedures	4

5.1	Test rules	4

6	System Architecture	6

7	Verification of Software functionality	7

7.1	GUI (Graphical User Interface) Function Screen Testing	7

7.1.1	Common Buttons	7

8	Equipment Addition	8

9	GUI Screens	9

9.1.1	Home	9

9.1.2	Change Password	9

9.2	Administration	10

9.2.1	Company	10

9.2.2	Comm Group	11

9.2.3	Department	12

9.2.4	User Group	13

9.2.5	Application Setup	15

9.2.6	Backup	16

9.2.7	System Diagnosis	16

9.2.8	Data Archive	16

9.3	Configuration	17

9.3.1	Application User	17

9.3.2	Equipment Config	18

9.3.3	Equipment Settings	19

9.3.4	Synchronize RTC	20

9.3.5	Equipment Status	20

9.3.6	Email/SMS Alert	21

9.3.7	Biometric RTC (If Applicable)	21

9.3.8	Timer Reset (Applicable Only In case of Photostability Machine/Thaw Chamber/Shaker Incubator/Co2 Incubator)	22

9.4	Real Time	22

9.4.1	Real time Summary	22

9.4.2	Real time Display	22

9.4.3	IO Status	22

9.4.4	Running Hours	23

9.5	Data Log Analysis	23

9.5.1	Manage Data Log	23

9.5.2	View Data Log	24

9.5.3	View Reviewed Data	25

9.5.4	View Approved Data	25

9.5.5	MKT Analysis	26

9.5.6	Alarm Log	26

9.6	Audit Trail	28

9.6.1	Alarm Audit Trail	28

9.6.2	Equipment Audit Trail	28

9.6.3	User Audit Trail	29

9.6.4	Email Audit Trail (Only if Email Alert Is Active)	30

9.6.5	SMS Audit Trail (If SMS Is Active)	30

9.6.6	Reviewed/Approved Audit Trail	31

9.7	Archive Analysis:-	32

9.7.1	Database Restore: - Start the Database Restore Utility in the restore utility folder and follow the steps for Database restore	32

9.7.2	Data Log Analysis	34

9.7.3	Audit Trail	35

9.7.4	Data Restore: - Once the Archive Test Over Restore the Archive Data base again as defined above in OQ Test Case No 8.7.1	35

9.8	Company Information	36

9.9	User Access Rights Groups Verification	37

10	Password Integrity	38

10.1	Login name Uniqueness / Password Complexity	38

10.2	Password Integrity	38

10.3	User Addition / Deactivation	39

10.4	User Access Rights Verification	41

11	Software Functionality testing	42

11.1	Power Failure Condition	42

11.2	Auto Backup	42

11.3	Auto Logout	42

11.4	Auto Password Save	42

12	Audit trail Functionality testing	43

13	References / Glossary	44

14	Deviation Report	45

15	Appendix	46

16	Conclusion	49

17	Approval of test results	49

# Introduction

Newtronic Lifecare Equipment Pvt Ltd. is into manufacturing of stability equipment’s such as Humidity chambers, BOD incubators, Photo stability Chambers and so on. The function of these chambers is to control temperature and/or humidity within acceptable range as per the set conditions. The equipment’s controller also performs the function of logging the data and alarm into its memory. The equipment are connected to the ICDAS Software. All equipment’s are connected through Ethernet to the software. The full version (server version) ICDAS 2.1 version 2.1.1 is already in function. Based on the customer requirement for desktop based software for limited chambers and limited functionality there was a need for desktop based software. So now we also have a new lite software named as ICDAS 2.1 Version 2.1.1 Lite  . This software is browser based desktop version software with features limited to single department and maximum 6 chambers. The software will automatically download data from all connected equipment’s and store its data in  SQL Database. The system will record temperature and /or Humidity of connected chambers and user will be capable to generate reports. The System has functionality of automatic backup on daily basis and security policies of windows.

# Protocol Pre approval

The responsible person signing the Pre-Approval page (page no: 1) had reviewed and approved the Operational Qualification protocol for Newtronic ICDAS 2.1 Software. Signing of this protocol indicates that the contents of the documents had been reviewed, all test procedures are accurate and the acceptance criteria are applicable for the intended purpose of this study.

# Brief Description

The ICDAS 2.1 software qualification and documentation is carried at Newtronic Life care Equipment Pvt. Ltd. for internal functionality testing of all forms and features in ICDAS 2.1 software. This qualification document ensures the software is tested and qualified before release and can be used for future reference.

The ICDAS 2.1 software for Newtronic make stability chambers is used for Online Monitoring of stability Equipment’s, Data and Alarm Logging, Email Generation and transmission (Optional), SMS generation and Transmission (Optional) for the Newtronic Equipment. The software is a browser based application and is 21 CFR ready software with all features available.

# Purpose

The purpose of this document is to verify test for,

- Forms, GUI Screens, function and menu bar items

- System Securities/Password Integrity

- Power Failure Availability of required utilities.

# Test procedures

The operation of Software shall be verified by reviewing the installed systems and physical parameters, using the test data sheets provided in the protocol. The test data sheets will be used to document the installation of the software.

## Test rules

The OQ forms are intended for entering test notations pertaining to individual tests and any deviations that may occur.

All test result must be completed manually during the test execution, as well as for the remarks areas.

If the test is not applicable please write "NA” (not applicable). All corrections must be dated and done by hand with sign. The original information has to be crossed out by a single line. The corrected information must be clearly visible.

Each completed tests has to be signed and dated.Deviations from the OQ specification that occur must be registered in the deviation protocol and recorded in the appendix.

The OQ is concluded if all acceptance criteria are fulfilled and the notations / deviations registered in the deviation protocol are remedied or accepted.

# System Architecture

SYSTEM ACHITECTURE DIAGRAM

ICDAS 2.1 Lite Software

MSSQL

Centralized

DB

Browser Based Application

TCP IP Network

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
| # Verification of Software functionality |  |  |  |  |  |
|  | ## GUI (Graphical User Interface) Function Screen Testing |  |  |  |  |
|  | Description | Describes the details of functionality of Forms/GUI screens and operations of main menu items of main screens/forms that is the task bar pane screens or more popularly called as the drop down menus. |  |  |  |
|  | Test Procedure | - Login into the ICDAS 2.1 Version 2.1.1 Lite Software with correct security level to enable all functions – here User with Admin rights enables all functions. - Expand the folders in the Main Menu window/explorer-pane, select the desired form and double-click on its icon to open its window. - Expand each & every folder and subfolders and open the forms. Verify & record the results. |  |  |  |
| ### Common Buttons |  |  |  |  |  |
|  |  | Add Button |  |  |  |
|  |  | Edit Button |  |  |  |
|  |  | Save Button |  |  |  |
|  |  | Delete Button |  |  |  |
|  |  | Find Button |  |  |  |
|  |  | Refresh Button |  |  |  |
|  |  | Print Button |  |  |  |
|  |  | Help Button |  |  |  |
|  |  | Exit Button |  |  |  |

| Sr. No. | Technical data Version |  | Observation |  |  | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | # Equipment Addition |  |  |  |  |  |  |
|  | Click On the Equipment Configuration option in the Configuration window | The Equipment Configuration Page Opens |  |  |  |  |  |
|  | Click On ADD to add a new equipment | The Add equipment window must open for entering of new equipment’s |  |  |  |  |  |
|  | Enter the following Details Equipment Name IP address Log Interval Door Access Type Click Save button | The details entered gets saved and the equipment gets added and displayed in the Equipment Config window | Details Entered Equipment Name:__________ IP Address:_______________ Log Interval:______________ Door Access Type:___________ Biometric Banner Text:_______________ Door Access User Name Status:________ Door Access User Details |  |  |  |  |
|  |  |  | User | User Name | User ID |  |  |
|  |  |  | Door Access 1 |  |  |  |  |
|  |  |  | Door Access 2 |  |  |  |  |
|  |  |  | Door Access 3 |  |  |  |  |
|  |  |  | Door Access 4 |  |  |  |  |
|  |  |  | Door Access 5 |  |  |  |  |
|  |  |  | Door Access 6 |  |  |  |  |

| Sr. No. |  | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- |
| # GUI Screens |  |  |  |  |  |  |
| ### Home |  |  |  |  |  |  |
|  | Login to Software and click on Home option |  | Home screen must open and must display the summary of equipment’s and unattended data/alarms |  |  |  |
|  | Grid View |  | Must display the summary of equipment’s in grid form |  |  |  |
|  | List View |  | Must display the summary of equipment’s in tabular listed form |  |  |  |
| ### Change Password |  |  |  |  |  |  |
|  |  | Invalid Details Entry | The software must not allow to change the password till all details are not entered properly |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Password Length | The Software must meet the password length |  |  |  |
|  | Enter the following Valid Details Old Password New Password Confirm New Password Click Change | Must update the old password of the user with new password |  |  |  |
|  | Click on logout to cross check the password change | Entering login name and new password must give access to software |  |  |  |

| ## Administration |  |
| --- | --- |
|  | ### Company |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Click on Company option in Administrator window | The company Info window will open and display Company Name Address Logo |  |  |  |
|  | Company Name | Displays/edits the entered Company details |  |  |  |
|  | Address | Displays/edits the entered address |  |  |  |
|  | Logo | Attach of company Logo of specified size |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Comm Group |  |  |  |  |
|  | Click on Group option in Administrator window | The communication Group window will open |  |  |  |
|  | To edit group details click on edit option and Enter the following Group Name Activation Key Click on Save | Entered Name Enter Activation Key Check the added/edited group in the Comm group list |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### Department |  |  |  |  |
|  | Click on Department option in Administrator window | The Department window will open and must display the departments |  |  |  |
|  | To edit new department select the department and click on edit option and Enter the following Department Details Name Comm Group Header Note Footer Note Archive Month | Details edited |  |  |  |
|  | Email Email System Email Alert Delay Alert Email Address 1 Alert Email Address 2 Alert Email Address 3 Alert Email Address 4 Alert Email Address 5 Supervisor Email Add1 Supervisor Email Add 2 Email Time | Details Entered/edited |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | SMS SMS System SMS Alert Delay Mobile User Name 1 Mobile User Name 2 Mobile User Name 3 Mobile User Name 4 Mobile User Name 5 Mobile Number 1 Mobile Number 2 Mobile Number 3 Mobile Number 4 Mobile Number 5 Click Save | Details Entered/edited |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### User Group |  |  |  |  |
|  | Click on User Group option in Administrator window | The User Group window will open and must display the added user groups |  |  |  |
|  | To add/edit new User group click on Add/edit and enter Name Details Select Access Rights Click on Save | Details Entered/edited |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### Application Setup |  |  |  |  |
|  | Click on Application Setup option in Administrator window | The Application setup window will open and display the details |  |  |  |
|  | The Allowable Fields can be added/edited Backup Local Path Backup Remote Path Backup Time Report Date/Time Stamp Password Change Email SMTP Settings SMTP Authentication SMTP Email SMTP Address SMTP User Name SMTP Password SMTP Port Secure Sockets Layer Email Signature SMS Settings Communication Port Parity Baud Rate Data Bits Stops Bits Click on Save | Details Entered/edited |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Test Email | Field to check email |  |  |  |
|  | Test SMS | Field to check SMS |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Backup |  |  |  |  |
|  | Click on Backup option in Administrator window Click on Take Backup | The Backup must happen at Path in Application Settings |  |  |  |
|  | ### System Diagnosis |  |  |  |  |
|  | Equipment Status | Displays the Status of Equipment |  |  |  |
|  | Service Status | Displays the Service status of equipment |  |  |  |
|  | Stop | Stops service polling |  |  |  |
|  | Reset | Resets service |  |  |  |
|  | Restart Server Service | Restart Server Service |  |  |  |
|  | Restart Local Service | Restart Local Service |  |  |  |
|  | ### Data Archive |  |  |  |  |
|  | Department Name | Department data to be archived |  |  |  |
|  | Data Archive Date Click Archive | Date till which the data gets archived if available |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ## Configuration |  |  |  |  |
|  | ### Application User |  |  |  |  |
|  | Click on the Application User option in the Configuration Window | The Application User window Opens |  |  |  |
|  | Click On add/edit button and enter the details User Name Login Name Password Comm.Group Department Name Group Status | Details Enter/Edit |  |  |  |
|  | Click On Save | User Add/Update message should be pop-up |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation |  |  | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | ### Equipment Config |  |  |  |  |  |  |
|  | #### Equipment Addition/Editing |  |  |  |  |  |  |
|  | Click On the Equipment Configuration option in the Configuration window | The Equipment Configuration Page Opens |  |  |  |  |  |
|  | Click On edit | The equipment detail window must open |  |  |  |  |  |
|  | Edit the Details Click Save button | The details entered gets saved | Details Edited Equipment Name:__________ Door Access User Details |  |  |  |  |
|  |  |  | User | User Name | User ID |  |  |
|  |  |  | Door Access 1 |  |  |  |  |
|  |  |  | Door Access 2 |  |  |  |  |
|  |  |  | Door Access 3 |  |  |  |  |
|  |  |  | Door Access 4 |  |  |  |  |
|  |  |  | Door Access 5 |  |  |  |  |
|  |  |  | Door Access 6 |  |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### Equipment Settings |  |  |  |  |
|  | Click On the Equipment Settings option in the Configuration window | The Equipment settings Page Opens and displays the added Equipment/IP address and Status |  |  |  |
|  | Select the equipment and click on edit option to edit the equipment parameters | The edit equipment window must open for editing the details - Equipement Parameter - Equipment Settings |  |  |  |
|  | Equipment Parameter | Displays the set colour configuration |  |  |  |
|  | Equipment Settings | Displays the set value conditions and the PID settings |  |  |  |
|  | Change the Parameter values Click on Save | The change values must get updated |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### Synchronize RTC |  |  |  |  |
|  | Click on the Synchronize RTC option in the Configuration Window | The Synchronize Date/Time window Opens and displays Equipment details |  |  |  |
|  | Select the Equipment Click on Save | Opens the Login Details window for authentication |  |  |  |
|  | Software will ask for confirmation and Login Details Click On Login | Enter valid login details Will update the RTC of the equipment with that of computer |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Equipment Status |  |  |  |  |
|  | Click On the Equipment Status option in the Configuration window | The Equipment status Page Opens and displays the added Equipment details |  |  |  |
|  | Select eqp click on whether to make Not active or Active based on the current status Click On Save | The status of the selected equipment must get change to new status |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- |
|  | ### Email/SMS Alert |  |  |  |  |  |
|  | Click on the Email/SMS alert option in the Configuration Window |  | The Email/SMS window Opens and displays added Equipment details |  |  |  |
|  | Select the Equipment Click on Edit |  | Opens the Alarms setting window for selection/deselection of alarms for Email/SMS |  |  |  |
|  | Select/Deselect the Alarms for sending via SMS/Email Click on Save |  | The Email/SMS must be sent only for the selected alarm events |  |  |  |
|  | Buttons |  | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Biometric RTC (If Applicable) |  |  |  |  |  |
|  | Click on the Biometric RTC option in the Configuration Window | The Biometric window Opens and displays the added Biometric details |  |  |  |  |
|  | Select the Equipment Click on Save | Opens the Login Details window for authentication |  |  |  |  |
|  | Software will ask for confirmation and Login Details Click On Login | Enter Valid Login details Will update the RTC of the selected Biometric |  |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |  |
| Sr. No. | Technical data Version |  |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | ### Timer Reset (Applicable Only In case of Photostability Machine/Thaw Chamber/Shaker Incubator/Co2 Incubator) |  |  |  |  |  |
|  | Click on the Lux/UV option in the Configuration Window | The Lux/UV window Opens and displays the Photostability Equipment |  |  |  |  |
|  | Click on the Thaw Timer option in the Configuration Window | The Thaw Timer reset Opens and displays the Thaw chamber |  |  |  |  |
|  | Click on the Speed Timer option in the Configuration Window | The Speed Timer reset Opens and displays the Shaker chamber |  |  |  |  |
|  | Click on the Sterilization Timer option in the Configuration Window | The Sterilization Timer reset Opens and displays the CO2 chamber |  |  |  |  |
|  | ## Real Time |  |  |  |  |  |
|  | ### Real time Summary |  |  |  |  |  |
|  | Click On the Real time summary in the Real time | The Real time summary window will open |  |  |  |  |
|  | Real Time Summary Window | Display the Online Offline status of eqp along with PV |  |  |  |  |
|  | ### Real time Display |  |  |  |  |  |
|  | Click On the Real time Display in the Real time | The Real time Display window will open |  |  |  |  |
|  | Real Time Display Window | Display Graph along with PV of all sensors |  |  |  |  |
|  | Replot | Replots the graph |  |  |  |  |
|  | ### IO Status |  |  |  |  |  |
|  | Click On the IO Status in Real time option | The IO status window will open |  |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
| b) | IO Status Window | Display the IO status of components installed in equipment with PV |  |  |  |
|  | ### Running Hours |  |  |  |  |
|  | Click On the Running Hours in Real time option | The Running Hours window will open |  |  |  |
|  | Running Hours Window | Must display the Components ON/OFF status along with running hours |  |  |  |
|  | ## Data Log Analysis |  |  |  |  |
|  | ### Manage Data Log |  |  |  |  |
|  | #### Review Data Log |  |  |  |  |
|  | Click On Review Data Log in the Data Log Analysis | The Review Data Log window will open |  |  |  |
|  | Select the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
|  | Click On Review | Opens the Login Details window for authentication |  |  |  |
|  | Check the View Reviewed Datalog for reviewed data | The reviewed data must get displayed in the View Reviewed data log |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | #### Approve Data Log |  |  |  |  |
|  | Click On Approve Data Log in the Data Log Analysis | The Approve Data Log window will open |  |  |  |
|  | Select the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
|  | Click On Approve | Opens the Login Details window for authentication |  |  |  |
|  | Check the View Approved Datalog for Approved data | The reviewed data must get displayed in the View Approved datalog |  |  |  |
|  | ### View Data Log |  |  |  |  |
|  | Click On the View Data Log in Data Log Analysis | The View Data log window will open |  |  |  |
|  | Enter the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
|  | Click On Graph | The Graph for the selected filtered details must get displayed |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### View Reviewed Data |  |  |  |  |
| a) | Click On the View Reviewed Data Log in Data Log Analysis | The View Reviewed Data log window will open |  |  |  |
| b) | Enter the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
| c) | Click On Graph | The Graph for the selected filtered details must get displayed |  |  |  |
| d) | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### View Approved Data |  |  |  |  |
|  | Click On the View Approved Data Log in Data Log Analysis | The View Approved Data log window will open |  |  |  |
|  | Enter the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
|  | Click On Graph | The Graph for the selected filtered details must get displayed |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | ### MKT Analysis |  |  |  |  |
|  | Click On MKT Analysis in the Data Log option | The MKT Analysis window will open |  |  |  |
|  | Enter the Filter Option Click Print | Print Preview of filtered data in PDF opens |  |  |  |
|  | Click On Print | Should print the displayed MKT for the selected sensor |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Alarm Log |  |  |  |  |
|  | Click On the Alarm Log option in the Audit Trail window | The Alarm Log window Opens |  |  |  |
|  | Enter the Filter Option | The Alarm logs for the filtered option must populate. |  |  |  |
|  | Print | Should open the Alarm print preview window |  |  |  |
|  | Print Button | The displayed alarms must get printed by clicking on the print command. |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | Select the check box in Alarm Log window to select the alarms Click On Save | Login Window must open for authentication. |  |  |  |
|  | Login Window Click Log In | Entering the login details with comments acknowledge the selected alarms and the details moves from the Alarm Log window to Alarm Audit Trail. |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ## Audit Trail |  |  |  |  |
|  | ### Alarm Audit Trail |  |  |  |  |
|  | Click On the Alarm Audit Trail option in the Audit Trail | The Alarm Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate. |  |  |  |
|  | Print | Print command Should open the Alarm Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Equipment Audit Trail |  |  |  |  |
|  | Click On the Equipment Audit Trail option in the Audit Trail | The Equipment Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate. |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | Print | Print command Should open the Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### User Audit Trail |  |  |  |  |
|  | Click On the User Audit Trail option in the Audit Trail | The User Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate. |  |  |  |
|  | Print | Print command Should open the User Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ### Email Audit Trail (Only if Email Alert Is Active) |  |  |  |  |
|  | Click On the Email Audit Trail option in the Audit Trail | The Email Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate and must print the displayed audit trail. |  |  |  |
|  | Print | Print command Should open the Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### SMS Audit Trail (If SMS Is Active) |  |  |  |  |
|  | Click On the SMS Audit Trail option in the Audit Trail | The SMS Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate and must print the displayed audit trail. |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Print | Print command Should open the Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ### Reviewed/Approved Audit Trail |  |  |  |  |
|  | Click On the Reviewed/Approved Audit Trail option in the Audit Trail | The Reviewed/Approved Audit Trail window Opens |  |  |  |
|  | Enter the Filter Option Click Print | The Audit Trail for the filtered details must populate and must print the displayed audit trail. |  |  |  |
|  | Print | Print command Should open the Audit Trail print preview window |  |  |  |
|  | Print Format | Select the different option in filter option to view reports in different format |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | Buttons | The Available buttons on the window must function as specified in the 6.1.1 |  |  |  |
|  | ## Archive Analysis:- For archive analysis restore the backup main data base data ie ICDAS2_1.bak file using data base restore utility. Select The validation Option for restoring the data. Once the features are tested restore the Archive back up ICDAS2_1_Archive.bak file again so as to avoid the mismatch in future. |  |  |  |  |
|  | ### Database Restore: - Start the Database Restore Utility in the restore utility folder and follow the steps for Database restore |  |  |  |  |
|  | Start the Database Restore Utility | The Restore utility must start |  |  |  |
|  | Database Restoration Option Open | Below option must be available for DB Restore 1 Restore Blank DB 2 Restore Existing DB |  |  |  |
|  | Select the “Restore Blank Database” Option to check the possibility of restoration the data backup” | The Error Message must get Populate |  |  |  |
|  | Select the “Already Existing Database” Option to restore the data backup” | The Data restore utility open with login screen & after enter valid details Window must get opened |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | The below option must be available - Select Path - Data Restore - Close - Main Database - Archive Database - Validation | Select The option to restore the Backup |  |  |  |
|  | Click On Select Path to restore the Backup | The Browse window must populate to select the Backup |  |  |  |
|  | Navigate the appropriate folder to select the wrong backup and click on Ok | The selected backup must get displayed in the utility window |  |  |  |
|  | Click on Main Database and click on restore | Error msg must populate |  |  |  |
|  | Click on Archive Database and click on restore | Error msg must populate |  |  |  |
|  | Click on Validation and click on restore | Error msg must populate |  |  |  |
|  | Navigate the appropriate folder to select the Correct ICDAS2_1.bak backup and click on Ok | The selected backup must get displayed in the utility window |  |  |  |
|  | Click on Main Database and click on restore | The selected file must get restored successfully |  |  |  |
|  | Check the data in Main Database for confirmation | The Files along with data must be correct |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | Navigate the appropriate folder to select the Correct archive ICDAS2_1_Archive.bak backup and click on Ok | The selected backup must get displayed in the utility window |  |  |  |
|  | Click on Archive Database and click on restore | The selected file must get restored successfully |  |  |  |
|  | Check the data in Archive Database for confirmation | The Files along with data must be correct |  |  |  |
|  | Navigate the appropriate folder to select the Correct ICDAS2_1.bak backup and click on Ok | The selected backup must get displayed in the utility window |  |  |  |
|  | Click on Validation and click on restore | The selected file must get restored successfully |  |  |  |
|  | Check the data in Archive Database for confirmation | The Files along with data must be correct |  |  |  |
|  | ### Data Log Analysis |  |  |  |  |
|  | View Data Log | View Datalog must open |  |  |  |
|  | View Reviewed Datalog | View Reviewed Datalog window open |  |  |  |
|  | View Approved Datalog | View Approved Datalog window must open |  |  |  |
|  | MKT Analysis | MKT window must open |  |  |  |
|  | Alarm Log | Alarm log window must open |  |  |  |
| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
|  | ### Audit Trail |  |  |  |  |
|  | Alarm Audit Trail | Alarm Audit Trail window must open |  |  |  |
|  | Equipment Audit Trail | Equipment Audit Trail window must open |  |  |  |
|  | User Audit Trail | User Audit Trail window must open |  |  |  |
|  | Email Audit Trail | Email Audit Trail window must open |  |  |  |
| e) | SMS Audit Trail | SMS Audit Trail window must open |  |  |  |
| f) | Reviewed/Approved Audit Trail | Reviewed/Approved Audit Trail window must open |  |  |  |
|  | ### Data Restore: - Once the Archive Test Over Restore the Archive Data base again as defined above in OQ Test Case No 8.7.1 |  |  |  |  |
|  | Navigate the appropriate folder to select the Correct archive ICDAS2_1_Archive.bak backup and click on Ok | The selected backup must get displayed in the utility window |  |  |  |
|  | Click on Archive Database and click on restore | The selected file must get restored successfully |  |  |  |
|  | Check the data in Archive Database for confirmation | The Files along with data must be correct |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ## Company Information |  |  |  |  |
|  | Company Information | This window gives the detail description about the company profile |  |  |  |

| Sr. No. | Test |  | Observation | Test result met Yes/No | Results and Comments |
| --- | --- | --- | --- | --- | --- |
|  | ## User Access Rights Groups Verification |  |  |  |  |
|  | Click on User Group option in Administrator window | The User Group window will open and must display the added user groups |  |  |  |
|  | To add/edit new User group click on Add/edit and enter Name Details Select Access Rights Click on Save | Details Entered/edited |  |  |  |
|  | Create 3 different User Groups | User Groups with defined rights must get created |  |  |  |
|  | 1st User Groups Created with rights | Define the rights for User Group ____________ |  |  |  |
|  | 2nd User Groups Created with rights | Define the rights for User Group ____________ |  |  |  |
|  | 3rd User Groups Created with rights | Define the rights for User Group ____________ |  |  |  |

| Sr. No. | Test | Description |  | Expected Result | Observation | Test result met Yes/No | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| # Password Integrity |  |  |  |  |  |  |  |
|  | Description |  | Verify the facilities of password change, auto password expiry, minimum password length, user name & password uniqueness, login/logout, account lockout facilities, user creation/deletion options in Software |  |  |  |  |
|  | ## Login name Uniqueness / Password Complexity |  |  |  |  |  |  |
|  | Password –Minimum Length |  | Check Password character length | Password length should be 8-15 characters. |  |  |  |
|  | Login name Uniqueness |  | Check Login uniqueness | System should not allow the generation of same users with unique login name. |  |  |  |
|  | Password Complexity |  | Check password complexity | Password combination should complex. |  |  |  |
|  | Account lock |  | Check wrong password up to 5 times | Username account should be blocked |  |  |  |
|  | ## Password Integrity |  |  |  |  |  |  |
|  | Combination |  | No Login name No Password | Login must not be allowed |  |  |  |
|  | Combination |  | Wrong Login name Wrong Password | Login must not be allowed |  |  |  |
|  | Combination |  | Right Login name Wrong Password | Login must not be allowed |  |  |  |
|  | Combination |  | Wrong Login name Right Password | Login must not be allowed |  |  |  |
|  | Combination |  | Right Login name and Right Password | Login must be allowed |  |  |  |

| Sr. No. | Test | Description | Expected Result | Observation | Test result met Yes/No | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- |
|  | ## User Addition / Deactivation |  |  |  |  |  |
|  | User Creation | Click on Application User to create a user | System should allow creation of user_____________ with defined rights |  |  |  |
|  | User Deletion if User not logged in anytime | Go to Application User, Select the user and click on delete | System should allow deletion of new user |  |  |  |
|  | User Deletion if User has logged in at least once | Go to Application User, Select the user and click on delete | System should not allow deletion of user if the user has not logged in previously |  |  |  |
|  | Compulsory Password Change | Login to software with new user created | The software must ask for compulsory password change during first login |  |  |  |
|  | User Password Expiry | Set the password expiry duration as 1 day in Application Setup and check for password change popup after expiry duration | The change password window must open when password duration expires |  |  |  |
| Sr. No. | Test | Description | Expected Result | Observation | Test result met Yes/No | Results and Comments |
|  | User Rights Modification | Go to Application User, double click on the user and change group to new group | System should allow modification of user rights. |  |  |  |
|  | User Deactivation | Go to Application User, double click on the user and change status from active to deactivate | System should allow Deactivation of user |  |  |  |

| Sr. No. | Test |  | Observation |  |  | Test result met Yes/No | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | ## User Access Rights Verification |  |  |  |  |  |  |
|  | Go to Application User Option in Configuration | The Application User window must open |  |  |  |  |  |
|  | Create 3 different user with different rights | The User with defined rights must get created | No of User | Name | User Group |  |  |
|  |  |  | 1 |  |  |  |  |
|  |  |  | 2 |  |  |  |  |
|  |  |  | 3 |  |  |  |  |
|  | Login to software with User 2 details | The software must give assess to the software for User 1________________ with defined user rights of ___________ |  |  |  |  |  |
|  | Login to software with User 1 details | The software must give assess to the software for User 2________________ with defined user rights of ___________ |  |  |  |  |  |
|  | Login to software with User 3 details | The software must give assess to the software for User 3________________ with defined user rights of ___________ |  |  |  |  |  |

| Sr. No. | Technical data Version |  | Observation | Test result met Yes/No | Results and Comments |
| --- | --- | --- | --- | --- | --- |
| # Software Functionality testing |  |  |  |  |  |
| ## Power Failure Condition |  |  |  |  |  |
|  | Description | The software should not be affected by power failure and should start automatically as per user settings after power has resumed. |  |  |  |
|  | Procedure | Turn OFF the computer system power for 30 seconds and restart: - Does the computer system start normally? - Does the software starts normally? |  |  |  |
| ## Auto Logout |  |  |  |  |  |
|  | Login to Software | Home screen must open |  |  |  |
|  | Keep the software and computer idle for 10 mins | Logon Screen must get open if the system is idle for more than 10 mins |  |  |  |
| ## Auto Password Save |  |  |  |  |  |
|  | Description | The software /browser must not popup any window for saving the password |  |  |  |
|  | Login to Software | Does the software/browser ask for password save option when logging in software? |  |  |  |
| ## Auto Backup |  |  |  |  |  |
|  | Check the Backup path for auo backup file | Backup namely - ICDAS2.1.bak - ICDAS2.1_Archive.bak Must be there at defined time |  |  |  |

| Sr. No. | Technical data Version |  |  |  |  |  |  | Test result met (Yes/No) | Results and Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Audit Trail For |  |  | Audit Trail Occurs After Record Modification? (Y/N/NA) | New & Old Data Stored In Audit Trail? (Y/N/NA) | Audit Trail Data Stored With Timestamp? (Y/N/NA) | Audit Trail Data Stored With Username? (Y/N/NA) |  |  |
| # Audit trail Functionality testing |  |  |  |  |  |  |  |  |  |
|  |  | Description | The verify the software generates audit trails of any changes made from the software |  |  |  |  |  |  |
|  |  | Alarm Audit Trail |  |  |  |  |  |  |  |
|  |  | Equipment Audit Trial |  |  |  |  |  |  |  |
|  |  | User Audit Trial |  |  |  |  |  |  |  |
|  |  | Email Audit Trail |  |  |  |  |  |  |  |
|  |  | SMS Audit Trail |  |  |  |  |  |  |  |
|  |  | Reviewed/ Approved Data log Audit trial |  |  |  |  |  |  |  |

# References / Glossary

| Abbreviation | Explanation |
| --- | --- |
| OQ | Operation Qualification |
| ICDAS | Intelligent Control Data Acquisition System |
| LAN | Local Area Network |
| Comm | Communication |
| PID | Proportion Integral Derivative control action |
| SMTP | Simple Mail Transfer Protocol |
| Email ID | Electronic Mail ID |
| MKT | Mean Kinetic Temperature |
| PDF | Portable Document Form |
| SMS | Short Message Service |
| IP | Internet protocol |
| LUX | Luminous Flux |
| UV | Ultra Violet |
| RTC | Real Time Clock |
| Config | Configuration |
| IO | Input /Output |

# Deviation Report

Report Number: ………………………………………………….

Deviations to the acceptance criteria that occurred during testing need to be stated in the deviation report. One deviation report must be created for each deviation and the report number to be indicated accordingly.

The deviation report can be copied as required.

| Description of problem | ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… |
| --- | --- |
| Measures for trouble shooting | ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… |
| Remarks | ……………………………………………………………………………………… ……………………………………………………………………………………… ……………………………………………………………………………………… |
| Executed By Verified/ accepted by | Name:………………………Date: . . . . . . . . . . . . . . . . Signature: . . . . .. . . . . . . . . . . . . . . Name:………………………Date: . . . . . . . . . . . . . . . . Signature: . . . . .. . . . . . . . . . . . . . |

# Appendix

| Annexure Number | Contents | Number of pages |
| --- | --- | --- |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |
| OQ_ICDAS2.1_Lite/ |  |  |

| Annexure Number | Contents | Number of pages |
| --- | --- | --- |

| Annexure Number | Contents | Number of pages |
| --- | --- | --- |

# Conclusion

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . .

# Approval of test results

The Operational Qualification is approved if all acceptance criteria are fulfilled and the notations / deficiencies registered in the deviation protocol are corrected or fully accepted.

Approved By:

| Tests executed | Name | Signature and Date |
| --- | --- | --- |
| Executed By | . . . . . . . . . . . . . . . . . . . | . . . . . . . . . . . . . . . . . . |
| All Test criteria have been fulfilled | Name | Signature and Date |
| Verified By | . . . . . . . . . . . . . . . . . . . | . . . . . . . . . . . . . . . . . . |
| All Test criteria have been fulfilled | Name | Signature and Date |
| Approved By | . . . . . . . . . . . . . . . . . . . | . . . . . . . . . . . . . . . . . . |